A REVIEW STUDY ON LPG AS AN ALTERNATIVE REFRIGERANT

Adem Ugurlu, Cihan Gokcol

ABSTRACT

This study reviews the literature, which has numerous works on the use of LPG, a hydrocarbon fuel utilized in many types of equipment, as an alternative refrigerant without any change in refrigerators, air conditioners, and similar cooling devices at various sizes. Referring to the results obtained from these studies LPG provides improvement of COP, reduction of the refrigerant amount used and energy saving compared to the other refrigerants in cooling devices draw attention of scientists. Outlining the results of the works given in this study, COP improvement, refrigerant reduction by mass, and energy saving reach to the values of 25.1%, 50%, and 90%, respectively, in case of using LPG instead of convensional refrigerants in different types of cooling machines.

Keywords: LPG, refrigerant, cooling machines, energy saving.

Introduction

In our days, improvement of cooling systems is a significant issue due to the concerns about energy efficiency and environmental reasons. Having good refrigerating behaviors for cooling devices, environmentally friendly hydrocarbon refrigerants -mainly propane, butane, and isobutane, which constitute LPG- have been researched by scientists in several appliances in recent years. The authors recommend in their studies that those hydrocarbon gases can be used in cooling devices as refrigerants instead of ozone layer damaging conventional refrigerant gases (Mohanraj et al., 2009). In addition to the better cooling features, hydrocarbons have other advantages such as being economical and available in large quantities (Mohanraj et al., 2009; Meyer, 1998; Peixoto, et al., 2000). Furthermore, they have an environment productive nature with zero ozone depletion and greenhouse effect potential (Mohanraj et al., 2009). The only noteworthy disadvantage of hydrocarbons is that they must be used carefully in cooling devices, since they are flammable (Meyer, 1998).

In this study, LPG has been compared with conventional refrigerants in terms of their relevant properties and obtained results from works encountered in literature when they are used in cooling devices. Multiple comparisons of the outstanding results of the studies will lead new researchers to work on the issue. Thus, properties of LPG constituting propane, butane, isobutane and some common refrigerants are given, and prominent results for different situations the authors found are reviewed with this investigation. LPG is a good substitute for common refrigerant gases is presented in conjunction with reasons.

LPG as a refrigerant

Refrigerants are used in heat engines such as heat pumps, air conditioners, and refrigerators as process gases circulating in a closed loop through the device.While corrosive, toxic, explosive, and flammable properties are undesirable characteristics for ideal refrigerants, low boiling point, high latent heat of vaporization, and high critical temperature are the appropriate thermodynamic properties. A comparison of some refrigerants to propane, butane, isobutene is given in Table 1.

Upon considering the table, it is clearly seen that LPG is a good substitute for common refrigerant gases with its thermodynamic and environmental features. For instance, LPG constituting gases, which are coded with the letter R referring that they are refrigerants and a number i.e. R290 for propane, R600 for butane, and R600a isobutane, have a higher latent heat of vaporization and lower boiling temperature compared to the other refrigerants (Fig.1 and Fig.2).

Higher latent heat of vaporization and lower boiling temperature of LPG allows it to have a higher cooling effect, and this provides more cooling with less mass flow rate. The meaning of a cooling machine that needs less refrigerant flow is the compressor of the machine operates less consuming lower energy. And this will also lower the environmental hazards arising from energy consumption. Furthermore, the compressor could be manufactured smaller and lighter decreasing the valume, weight and price of the system.

On the other hand, there are two features of refrigerants crucial for the environment. They are ODP (ozone depletion potential) and GWP (global warming potential). When we check the table, we see that those values of LPG are little or nothing compared to other refrigerants. ODP value of LPG is zero and its GWP value is 3, which the other refrigerants have a GWP of over 1300. Zero ODP value of LPG shows it is not harmful to the ozone layer, and compared to other commonly used refrigerants, nearly a thousand times lower GWP value of LPG indicates that it does not contribute to the global warming.

The only disadvantage of LPG is its explosion feature, as it is seen from the table. For this reason, LPG should be handled with carefully in cooling devices, as that is also carried out in other usage of all hydrocarbons.

Studies on the use of LPG as an alternative refrigerant

In literature, there are numerous studies that LPG constitutes conventional refrigerants as an alternative without any change in refrigerators, air conditioners and similar cooling devices at various sizes. In this respect, prominent ones of those studies between the years of 1991-2015 are given in Table 2 as examples. When we refer to these studies, following results could be obtained in general draw attention: improvement of COP, reduction of the refrigerant amount used, and energy saving in the cooling machines. Increase in COP, decrease in refrigerant charge, and decrease in energy consumption have been found between the values of 1-25.1%, 14.6-50%, and 3-90%, respectively. There have been nearly no negative results in the authors’ experiments and calculations, and the worst result of LPG has been similar performance and similar capacity. Thus, it has been understood from the studies that LPG can be used as a refrigerant; even it has a higher cooling effect than the other refrigerants. The reason that LPG has better cooling properties comparing to the other refrigerants is mostly because of its higher latent heat of vaporization.

Table1: Comparison of some refrigerants (Mohanraj et al., 2009; World Meteorological Organization, 1991; IPCC, 1994; Maclaine-cross and Leonardi, 1995; Wongwises, et al., 2006; Calm and Hourahan, 2001; Rasti et al., 2012; Jwo et al., 2009; Hesselgreaves, 2001; Ed. Kreith, 2000; Leonardi and Maclaine-cross, 1995; Kara, 2008; Beser, 1997; Özkol, 1999; Dossat, 1997; NIST, 2002; Hwang et al., 2004; Beşer, 1998; Şengür, 2005)

| Refrigerant | R11 | R12 | R22 | R134a | R290 | R600 | R600a |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Common name | Trichloro fluoro methane | Dichlorodifluoromethane | Chloro difluoromethane | 1,1,1,2-Tetrafluoroethane | Propane | Butane | Isobutane |
| Chemical formula | CCl3F | CCl2F2 | CHClF2 | F3CCH2F | C3H8 | C4H10 | C4H10 |
| Refrigerant class | CFC | CFC | HCFC | HFC | HC | HC | HC |
| Molecular mass (g/mol) | 137.37 | 120.91 | 86.47 | 102.03 | 44.1 | 58.13 | 58.13 |
| Density (kg/L) | 1.47 (21.1°C) | 1.34 (30°C) | 1.21 (21.1°C) | <1.22 | 0.500 (20°C) | 0.579 (20°C) | 0.564 |
| Vapor density (air=1) | 4.8 | 4.2 | 3 | 3.5 | 1.6 | 2 | 2 |
| Boiling point (°C) | -23.8 | -29.8 | -40.8 | -26.1 | -42.1 | -0.4 | -11.7 |
| Critical point (°C) | 198 | 111.8 | 96.2 | 101.08 | 96.67 | 152 | 135 |
| Critical pressure (bar) | 44.1 | 41.1 | 49.9 | 40.6 | 42.5 | 38 | 36.5 |
| ODP | 1 | 1 | 0.07 | 0 | 0 | 0 | 0 |
| GWP (100 years) | 3400 | 8500 | 1700 | 1300 | 3 | 3 | 3 |
| Latent heat of vaporization at 1 atm (kJ/kg) | 227.3 | 165.24 | - | 216.87 | 427.8 | 385.2 | 364.25 |
| Life in the atmosphere (years) | - | 130 | 15 | 16 | <1 | <1 | <1 |
| Explosion limits (in air% by volume) | Not explosive | Not explosive | - | Not explosive | 2.3 - 7.3 | 1.6 - 6.5 | 1.8 - 8.4 |

Figure 1: Boiling points of common refrigerants

Figure 2: Latent heat of vaporization of common refrigerants

Table 2: Studies on the use of LPG as an alternative refrigerant by year

| Date | Author(s) | Appliance | Refrigerant | Alternative | Results |
| --- | --- | --- | --- | --- | --- |
| 1991 | Dieckmann et al. | Automobile air conditioner | - | HC | * 4% decrease in fuel consumption. |
| 1994 | Rivis and Bidone | Theoretical | R12 | 50% propane + 50% isobutane | * Similar performance. * 3.2 COP value in Te=-15°C. |
| 1994 | Abboud | Automobile air conditioner | R12 | HC | * 13% decrease in energy consumption. |
| 1995 | Richardson and Butterworth | Refrigerator | R12 | 50% propane + 50% isobutane | * Increase in COP. * Lower refrigerant amount. * Lower compressor body temperature. |
| 1995 | Leonardi and Maclaine-cross | Automobile air conditioner | R12 | LPG | * 10% higher refrigerating effect. |
| 1995 | Liu et al. | Refrigerator | R12 | 70% propane + 30% butane | * Lower energy consumption. |
| 1995 | Parmar | Automobile air conditioner | R12 | HC | * 13% decrease in energy consumption. |
| 1996 | Jung et al. | Refrigerator | R12 | 20-60% propane + 80-40% isobutane | * 2.3% increase in COP. * 3% energy saving from the total energy consumption. |
| 1996 | Choi et al. | Heat pump | R22 | Propane / isobutane | * Better COP value. * Decrease in capacity. |
| 1998 | Meyer | Theoretical | R22 | LPG | * Almost the same cooling capacity. |
| 1998 | Alsaad and Hammad | Refrigerator | R12 | 24% propane + 58% butane + 18% isobutane | * 3.4 COP value at Te=-15°C and Tc=27°C. |
| 1998 | Purkayastha and Bansal | Heat pump | R22 | Propane | * 18% increase in COP. |
| 1999 | Hammad and Alsaad | Refrigerator | R12 | 50% propane + 38.3% butane + 11.7% isobutane | * Higher COP. |
| 1999 | Ghodbane | Automobile air conditioner | R134a | Propane | * Increase in performance. |
| 1999 | Jung et al. | Automobile air conditioner | R12 | 60% propane + 40% isobutane | * Similar performance. |
| 2000 | Jung et al. | Refrigerator | R12 | 20-60% propane + 80-40% isobutane | * 2.3% increase in COP. * About 3-4%increase in energy efficiency. |
| 2000 | Peixoto et al. | Water cooler | R134a | Isobutane | * Improvement in COP. * 13% decrease in energy consumption. * 50% decrease in refrigerant amount. |
| 2000 | Chang et al. | Heat pump | R22 | Propane | * Improvement in COP. |
| 2003 | Akash and Said | Refrigerator | R12 | 30% propane + 55% butane + 15% isobutane | * 3-4 times higher cooling capacity. |
| 2003 | Elefsen et al. | Ice cream machine | R404a | Propane | * 90% decrease in energy consumption. |
| 2003 | Chaichana et al. | Heat pump | R22 | Propane | * Similar performance. |
| 2003 | Joudi et al. | Automobile air conditioner | R12 | Propane / isobutane | * Similar results. |
| 2004 | Urchueguiaet al. | Compressor | R22 | Propane | * 13-20% decrease in cooling capacity. * 1-3% increase in COP value. |
| 2005 | Wongwises and Chimres | Refrigerator | R134a | 60% propane + 40% butane | * Lower energy consumption due to higher latent heat of LPG. |
| 2006 | Fatouh and El Kafafy | Refrigerator | R134a | 60% propane + 20% butane + 20% isobutane | * 7.6% higher COP. * 4.3% decrease in power. |
| 2006 | Park and Jung | Household air conditioners | R22 | Propane | * Similar cooling capacity. * Higher COP. |
| 2006 | Wongwises et al. | Automobile air conditioner | R134a | 50% propane + 40% butane + 10% isobutane | * Increase in COP. * Similar cooling capacity. |
| 2008 | Mani and Selladurai | Vapor compression refrigeration system | R12 and R134a | Propane / isobutane | * Higher cooling capasities between 19.9-50.1% from R12, and 28.6-87.2% from R134. * 3.9-25.1% higher COP from R12. |
| 2009 | Jwo et al. | Refrigerator | R134a | 50% propane +50% isobutane | * Better cooling effect. * 4.4% saving from the total consumed energy. * 40% decrease in refrigerant amount used by mass. |
| 2009 | Mohanraj et al. | Refrigerator | R134a | 45.2% propane + 54.8% isobutane | * 11.1% decrease in energy consumption of the compressor. |
| 2009 | Ravikumar et al. | Automobile air conditioner | R12 | R134a / propane / isobutane | * Similar performans. |
| 2010 | Dalkilic and Wongwises | Vapor compression refrigeration system | R12 and R22 | 40% propane + 60% isobutane | * The most suitable alternative refrigerant mixture. |
| 2012 | Rasti et al. | Refrigerator | R134a | 56% propane + 44% isobutane | * 13% decrease in operating time of the compressor. * 5.3% decrease in daily energy consumption. |
| 2013 | Rasti et al. | Refrigerator | R134a | 46% isobutane + 54% propane / isobutane | * 7-14% decrease in energy consumption. * 14.6-18.7% decrease in refrigerant charge. |
| 2014 | Teng and Yu | Refrigerator | R134a | 65% propane + 35% isobutene / 50% propane + 50% isobutene / isobutane | *40% decrease in refrigerant charge. * Lower electricity consumption. * Lower on-time ratio. |
| 2015 | El-Morsi | Theoretical | R134a | Propane / butane | * Increase in COP. |

Conclusion

LPG is a kind of hydrocarbon gas, consisting of propane, butane, and isobutene at different rates, and is used mostly as fuel in heating appliances, cooking equipment, and vehicles.The little-known feature of LPG is its good refrigerating property and with that it can be used in cooling appliances as a refrigerant. There are numerous works on the usage of LPG as a refrigerant in cooling devices.

This study reviews the comparison of LPG to some common refrigerants in respect of cooling properties and featured results of works that LPG is used as a refrigerant in cooling devices substituting other refrigerants. As understood from the properties of LPG and the aforementioned works, LPG can be used as a refrigerant in refrigerators, air conditioners, and other cooling devices without any change providing higher COP, lower refrigerant amount, and energy consumption. COP improvement, refrigerant reduction by mass, and energy saving reach to the values of 25.1%, 50%, and 90%, respectively, in case of using LPG instead of convensional refrigerants in different types of cooling machines.

Benefitting from the refrigerating feature of LPG, cooling devices can be charged directly with LPG, those appliances can be improved for a higher efficiency, new equipments can be designed, and even some novel systems like integrated fuel and air conditioning systems for LPG powered vehicles can be produced. As authors of this study, we suggest that all equipments that utilize LPG as a fuel or so on should be checked and modified with small changes if possible to take advantage of this refrigerating effect of LPG.

References

Abboud, B. (1994). Field trials of propane/butane in automotive air-conditioning, B.E. thesis, School of Mechanical and Manufacturing Engineering, The University of New South Wales, Sydney.

Akash, B.A. and Said, S.A. (2003). Assessment of LPG as a possible alternative to R-12 in domestic refrigerators, Energy Conversion and Management, 44, 381–388.

Alsaad, M.A. and Hammad, M.A. (1998). The application of propane/butane mixture for domestic refrigerators, Applied Thermal Engineering, 18, 911-918.

Beser, E. (1997). Sogutucu maddelerle ilgili dünyada ve Türkiye'deki gelişmeler, IV. Ulusal Tesisat Mühendisligi Kongresi ve Sergisi, Bildiriler Kitabı, 2, 679-697.

Beşer, E. (1998). Soğutucu maddelerle ilgili dünyada ve Türkiye'deki gelişmeler, Mühendis ve Makine, 39, 458, 15-26.

Calm, J.M. and Hourahan, G.C. (2001). Refrigerant data summery, Engineering Systems, 18, 74–88.

Chaichana, C., Lu, A. and Charters, W.W.S. (2003). Natural working fluids for solar boosted heat pumps, International Journal of Refrigeration, 26, 637–643.

Chang, Y.S., Kim, M.S. and Ro, S.T. (2000). Performance and heat transfer characteristics of hydrocarbon refrigerants in a heat pump system, International Journal of Refrigeration, 23, 232–242.

Choi, D.K., Domanski, P.A. and Didion, D.A. (1996). Evaluation of flammable refrigerants for use in water-to-water residential heat pump. IIR applications for natural refrigerants, In: Proceedings, Aarhus, Denmark, 467–476.

Dalkilic, A.S. and Wongwises, S. (2010). A performance comparison of vapour-compression refrigeration system using various alternative refrigerants, International Communications in Heat and Mass Transfer, 37, 1340–1349.

Dieckmann, J., Bentley, J. and Varone, A. (1991). Non-inert refrigerant study for automotive applications final report, US Department of Energy, 76.

Dossat, R.J. (1997). Principles of refrigeration, Prentice Hall, 512, New Jersey.

Ed. Kreith, F. (2000). The CRC handbook of thermal engineering, CRC Press LLC.

Elefsen, F., Nyvad, J., Gerrard, A. and VanGerwen, R. (2003). Field test of 75 R404A and R290 ice cream freezers in Australia, ARIAH Journal, 24–27.

El-Morsi, M. (2015). Energy and exergy analysis of LPG (liquefied petroleum gas) as a drop in replacement for R134a in domestic refrigerators, Energy, 86, 344-353.

Fatouh, M. and El Kafafy, M. (2006). Experimental evaluation of a domestic refrigerator working with LPG, Applied Thermal Engineering, 26, 1593–1603.

Ghodbane, M. (1999). An investigation of R152a and hydrocarbon refrigerants in mobile air conditioning, SAE  Technical Papers, Paper No. 1999-01-0874, Society of Automotive Engineers.

Hammad, M.A. and Alsaad, M.A. (1999). The use of hydrocarbon mixtures as refrigerants in domestic refrigerators, Applied Thermal Engineering, 19, 1181-1189.

Hesselgreaves, J.E. (2001). Compact heat exchangers, Elsevier Science & Technology Books.

Hwang, Y., Jin, D.H. and Radermacher, R. (2004). Comparison of hydrocarbon R-290 and two HFC blends R-404a and R-410a for medium temperature refrigeration applications, Final Interim Report, University of Maryland.

IPCC, (1994). Radiative forcing of climate change, The 1994 report of the scientic assessment working group of IPCC, Summary for policy makers, Intergovernmental Panel on Climate Change, 28.

Joudi, K.A., Mohammed A.S. and Aljanabi, M.K. (2003). Experimental and computer performance study of an automotive air conditioning system with alternative refrigerants, Energy Conversion Management, 44, 2959–2976.

Jung, D., Kim, C.B., Lim, B.H. and Lee, H.W. (1996). Testing of a hydrocarbon mixture in domestic refrigerators, ASHRAE Transactions, 3, 1077–1084.

Jung, D., Kim, C.B., Song, K. and Park, B. (2000). Testing of propane/izobutane mixture in domestic refrigerators, International Journal of Refrigeration, 23, 517-527.

Jung, D.S., Park, B. and Lee, H. (1999). Evaluation of supplementary/ retrofit refrigerants for automobile air conditioning charged with CFC12, International Journal of Refrigeration, 22, 558–568.

Jwo, C.S., Ting, C.C. and Wang, W.R. (2009). Efficiency analysis of home refrigerators by replacing hydrocarbon refrigerants, Measurement, 42, 697–701.

Kara, A. (2008). Evaporatif kondenser tasarımı, imalatı ve deneysel olarak incelenmesi, Bilim Uzmanlıgı Tezi, Karabük Üniversitesi.

Leonardi, E. and Maclaine-cross, I.L. (1995). Performance and safety of LPG refrigerants, Proceeding of the Fuel for Change Conference of the Australian LPG Association Ltd, 149-168.

Liu, B.Y., Tomasek, M. and Radermacher, R. (1995). Experimental results with hydrocarbon mixtures in domestic refrigerator/freezers, ASHRAE Trans., 101, 1415–1421.

Maclaine-cross, I. L. and Leonardi, E. (1995). Hydrocarbon Refrigerant Risk in Car Air-Conditioners, International CFC and Halon Alternatives Conference, Washington DC.

Mani, K. and Selladurai, V. (2008). Experimental analysis of a new refrigerant mixture as dropin replacement for CFC12 and HFC134a, International Journal of Thermal Sciences, 47, 1490–1495.

Meyer, J.P. (1998). Evaluation of LPG as a refrigerant in air conditioning and refrigeration, Mechanical Technology, December, 7-12.

Mohanraj, M., Jayaraj, S. and Muraleedharan, C. (2009). Environment friendly alternatives to halogenated refrigerants - A review, International Journal of Greenhouse Gas Control, 3, 108-119.

Mohanraj, M., Jayaraj, S., Muraleedharan, C. and Chandrasekar, P. (2009). Experimental investigation of R290/R600a mixture as an alternative to R134a in a domestic refrigerator, International Journal of Thermal Sciences, 48, 1036–1042.

NIST, (2002). REFPROP-Reference Fluid Thermodynamic and Transport Properties V7.0.

Özkol, N. (1999). Uygulamalı soğutma tekniği, TMMOB Makine Mühendisleri Odası, Yayın No: 115, 714, Ankara.

Park, K.J. and Jung, D.S. (2006). Thermodynamic performance of HCFC22 alternative refrigerants for residential air conditioning applications, Energy and Buildings, 39, 675–680.

Parmar, A.S. (1995). Performance of hydrocarbon refrigerants in motor car air- conditioning, B.E. Thesis, School of Mechanical and Manufacturing Engineering, The University of New South Wales, Sydney.

Peixoto, R., Epof, S. and Parra, D. (2000). Experimental Investigation on the Performance of Commercial Freezers Using Refrigerant R600a, IIF-IIR Commission B1, B2, E1 and E2, Purdue University, USA, 159–165.

Purkayastha, B. and Bansal, P.K. (1998). Experimental study on HC290 and a commercial liquefied petroleum gas (LPG) mix as suitable replacements for HCFC22, International Journal of Refrigeration, 21, 213–217.

Rasti, M., Aghamiri, S.F. and Hatamipour, M.S. (2013). Energy efficiency enhancement of a domestic refrigerator using R436A and R600a as alternative refrigerants to R134a, International Journal of Thermal Sciences, 74,  86-94.

Rasti, M., Hatamipour, M.S., Aghamiri, S.F. and Tavakoli, M. (2012). Enhancement of domestic refrigerator’s energy efficiency index using a hydrocarbon mixture refrigerant, Measurement, 45, 1807–1813.

Ravikumar, T.S. and Lal, D.M. (2009). On-road performance analysis of R134a/R600a/R290 refrigerant mixture in an automobile air-conditioning system with mineral oil as lubricant, Energy Conversion and Management, 50, 1891–1901.

Richardson, R. and Butterworth, J. (1995). The performance of propane/isobutane mixtures in vapor compression systems, International Journal of Refrigeration, 18, 1, 58-62.

Rivis, E. and Bidone, A. (1994). Isobutane/propane mixtures: comparison with traditional refrigerants, The Day After Conference, Padua, Italy, 345-353.

Şengür, S. (2005). Buzdolaplarında alternatif soğutucu akışkan olarak LPG kullanılmasının deneysel olarak araştırılması, Yüksek Lisans Tezi, Fırat Üniversitesi.

Urchueguia, J.F., Corberan, J.M., Gonzalvez, J. and Diaz, J.M. (2004). Experimental characterization of a commercial–size scroll and reciprocating compressor working with R22 and propane (R290) as refrigerant, Ecobibrium Journal of AIRAH, 23–25.

Wongwises, S. and Chimres, N. (2005). Experimental study of hydrocarbon mixtures to replace HFC134a in domestic refrigerators, Energy Conversion and Management, 46, 85–100.

Wongwises, S., Kamboon, A. and Orachon, B. (2006). Experimental investigation of hydrocarbon mixtures to replace HFC-134a in an automotive air conditioning system, Energy Conversion and Management, 47, 1644–1659.

World Meteorological Organization, (1991). Scientific assessment of ozone depletion:1991, Global ozone research and monitoring project - Report No. 25, Geneva.

Yu, C.C. and Teng, T.P. (2014). Retrofit assessment of refrigerator using hydrocarbon refrigerants, Applied Thermal Engineering, 66, 507-518.

Assistant Professor, Kirklareli University, adem.ugurlu@klu.edu.tr

Lecturer, Kirklareli University, cihan.gokcol@klu.edu.tr